## 1. LOS Asset Hierarchy Template
Service | Program Service Objectives | Community Levels of Service | Service Division | Supporting Asset Classes | Target Asset Levels of Service (by Asset Class) | Current Asset Levels of Service
[6 empty] | Asset Class Average | Distribution by Asset Rating
[7 empty] | % | % | % | % | %
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
Note on A1: Consistent with Asset hierarchy
Note on B1: A general service statement reflecting the desired level of service to the customer. Sources: Strategic Plan, Council Directive. See examples in the catalogue
Note on C1: General service statements on what the customer expects to receive from the service. See examples in the catalogue.
Note on D1: Should be consistent with asset hierarchy
Note on E1: Should be consistent with asset hierarchy
Note on F1: Refer to Condition Rating and General Performance Rating sheets for ratings and recommended targets.
Note on G2: The averaged level of service for the asset class.
Note on H2: Breakdown of the assets per the ratings and ranges on the Condition Rating and General Performance Rating sheets.

## 2. LOS Asset Hierarchy e.g. WW
Service | Program Service Objectives | Community Levels of Service | Service Division | Supporting Asset Classes | Target Asset Levels of Service (by Asset Class) | Current Asset Levels of Service
[6 empty] | Asset Class Average | Distribution by Asset Rating
[7 empty] | % | % | % | % | %
Wastewater | Safe, reliable and efficient wastewater services | Wastewater is fully treated before discharge to the environment | Collection | Collection Sewers | Condition | Condition
[5 empty] | Pipes: PACP = 3 | PACP = 2 | 70 |  | 30
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
|  |  |  | Trunk Sewers | Condition | Condition
[5 empty] | Pipes: PACP = 3 | PACP = 2
|  | System capacity is adequate to carry all wastewater flows |  |  | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
|  |  |  | Pumping Stations | Condition | Condition
[5 empty] | Mechanical Process Systems = "Good" | Fair |  | 40 | 60
[5 empty] | Electrical Process Systems = "Good" | Fair |  | 40 | 60
[5 empty] | Civil Collection Assets = 'Good' | Good |  | 100
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good | Fair |  | 30 | 60
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Fair |  | 50 | 50
[5 empty] | Environmental Resiliency = Good | Good |  | 100
|  | The system is efficiently designed and managed | Treatment | Preliminary Treatment | Condition | Condition
[5 empty] | Mechanical Process Systems = "Good" | Fair |  | 50 | 50
[5 empty] | Electrical Process Systems = "Good" | Fair |  | 50 | 50
[5 empty] | Civil Treatment Assets = 'Good' | Good | 50 | 50
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Good |  | 100
[5 empty] | Environmental Resiliency = Good | Poor |  |  |  | 100
|  |  |  | Primary Treatment | Condition | Condition
[5 empty] | Mechanical Process Systems = "Good" | Fair |  | 50 | 50
[5 empty] | Electrical Process Systems = "Good" | Fair |  | 50 | 50
[5 empty] | Civil Treatment Assets = 'Good' | Good | 50 | 50
|  | The water system is kept in good condition |  |  | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Good |  | 100
[5 empty] | Environmental Resiliency = Good | Poor |  |  |  | 100
|  |  |  | Secondary Treatment | Condition | Condition
[5 empty] | Mechanical Process Systems = "Good" | Fair |  | 50 | 50
[5 empty] | Electrical Process Systems = "Good" | Fair |  | 50 | 50
[5 empty] | Civil Treatment Assets = 'Good' | Good | 50 | 50
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Good |  | 100
[5 empty] | Environmental Resiliency = Good | Poor |  |  |  | 100
Note on A1: Consistent with Asset hierarchy
Note on B1: A general service statement reflecting the desired level of service to the customer. Sources: Strategic Plan, Council Directive. See examples in the catalogue
Note on C1: General service statements on what the customer expects to receive from the service. See examples in the catalogue.
Note on D1: Should be consistent with asset hierarchy
Note on E1: Should be consistent with asset hierarchy
Note on F1: Refer to Condition Rating and General Performance Rating sheets for ratings and recommended targets.
Note on G2: The averaged level of service for the asset class.
Note on H2: Breakdown of the assets per the ratings and ranges on the Condition Rating and General Performance Rating sheets.

## 3 .Serv Object CLOS Statements
Service | Examples of Service Objective Statements | Examples of Community Levels of Service
Wastewater | Safe, reliable and efficient wastewater services | Wastewater is fully treated before discharge to the environment
Odours are minimized
System capacity is adequate to carry all wastewater flows
The system is efficiently designed and managed
The wastewater system is kept in good condition

## 4. Cond Ratings Wastewater
Asset Types | Notes for Determining Asset Levels of Service | Asset Condition Ratings and Corresponding Likelihood of Failure1, 2, 3 |  |  |  |  | Additional Notes
|  | Likelihood of Failure Very Unlikely (Estimated beyond 20 yrs. or >10%) | Likelihood of Failure Unlikely (Estimated in 11-20 yrs. or 10%-30%) | Likelihood of Failure Possible (Estimated in 6-10 yrs. or 30%-60%) | Likelihood of Failure Likely (Estimated in 1-5 yrs. or 60%-90%) | Likelihood of Failure Very Likely or Certain (Estimated in less than 1 yr. or Now or <90%)
- Trunk Sewers - Local Collection Sewers - Forcemains | A target PACP = 3 (Fair) or ERUSL = 11 - 20 years is recommended for Trunk, Local Collection Sewers and Forcemains due to: - a significant to high importance to community services - a moderate to significant risk liability (health and safety, environment, financial cost, municipal reputation) - to provide the opportunity to cost effectively reline the pipe before it becomes to dysfunctional to do so and needs to be replaced - the need for additional planning and financing of sewer pipes located in environmentally sensitive areas or extra deep locations | PACP = 1 or 2 Very Good or Good Pipe segment has minor defects - pipe unlikely to fail for at least 20 years. OR ERUSL>20 years (When estimating pipe condition based on age and material) | PACP = 3 Fair Pipe segment has moderate defects - deterioration may continue, at a ten to twenty year timeframe. OR ERUSL is 11-20 years (When estimating pipe condition based on age and material) Spot repair zone. Use of internal spot repairs or possibly some section relining to extend useful service life (subject to CCTV assessment). | PACP = 4 Poor Pipe segment has severe defects - risk of failure within the next five to ten years OR ERUSL 6-10 years (When estimating pipe condition based on age and material) Pipe relining zone. Pipe relining is usually a viable option to restore the pipe to a Good or Very Good condition (subject to CCTV assessment). | PACP = 5 Very Poor Pipe segment has failed or will likely fail within the next five years - requires immediate attention. OR ERUSL is 1-5 years (When estimating pipe condition based on age and material) Pipe replacement zone. Pipe relining may not be a viable option if the pipe is out of round or partially collapsed (subject to CCTV assessment). | PACP = 5 Failed Pipe segment has failed or will likely fail within the next five years - requires immediate attention. OR ERUSL <1 year or beyond EURSL or failed (When estimating pipe condition based on age and material) Pipe replacement zone. Pipe has failed/collapsed or in severe condition (subject to CCTV assessment). | When using asset age to estimate asset condition, consider maintaining a conservative estimate of the total useful service life until such time as condition assessments data becomes available. Note that ERUSL in absence of PACP information should be used to prioritize CCTV investigation to determine actual pipe conditions and determine future corrective actions. Source (except in italics): PACP (Pipeline Assessment Certification Program) - Measures, ranges and descriptions are sourced from the National Association of Sewer Service Companies (NASSCo). PACP 5 recommendations on whether the pipe is likely to fail within 5 years or has failed made at the time of the inspection.
Wastewater treatment and collection mechanical and electrical assets such as pumps, motors, motor control centres, centrifuges, conveyors, skimmers, scrapers, bridges, generator units etc. as part of: - Pumping Stations/Pumping Systems - Pre-Treatment/Pre-Treatment Systems - Primary Treatment/ Primary Treatment Systems - Secondary Treatment/Secondary Treatment Systems - Aeration and Disinfection Systems - Biosolids Treatment/Biosolids Treatment Systems - Standby Power | Targets, ranges and descriptions intended for assets with an estimated useful service life of at least 20 years. A target of "Good" or ERUSL = 11-20 years (when estimating condition based on age) is recommended for the assets/asset systems due to a variety of factors: - a significant to high importance to community services - a significant risk liability (health and safety, environment, financial cost, municipal reputation) - the potential complexities and additional time necessary to plan and design the replacement or rehabilitation of the assets/asset systems (say >5 years) - the potentially significant financial value of the assets/asset systems requiring extra time to accumulate necessary financing for possible full replacement or reconstruction (say >5 years) - some assets can benefit from rehabilitation strategies to extend asset life and defer reconstruction/replacement costs before the assets become too worn or dysfunctional to make such strategies feasible - the assets/assets systems may be expensive to operate and need to be efficient to minimize costs A target of "Fair" or ERUSL = 6-10 years (when estimating condition based on age) may be considered due to a variety of factors: - a moderate or low importance to service delivery - a moderate or low risk liability (health and safety, environment, financial cost, municipal reputation) - there is little complexity or uniqueness to the assets/asset systems thus requiring less planning and design time (< 5 years) - a moderate or low value to replace, reconstruct or rehabilitate the assets/asset systems thus requiring a shorter time to accumulate necessary financing (say < 5 years) - proactive rehabilitation strategies are generally not cost-effective or non-existent and the assets/asset systems are better suited to a straightforward change-out or replacement. - Operating costs are relatively low | The assets are rated 'Very Good'. - Fit for the future. - Well maintained, in good condition, new or recently rehabilitated. - Minor defects and/or wear AND/OR ERUSL>20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Good'. - Adequate for now. - Modest defects and/or wear. AND/OR ERUSL = 11-20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Fair'. - Shows signs of deterioration and some elements exhibit deficiencies. - May require attention. - Moderate defects and/or wear AND/OR ERUSL= 6-10 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Poor'. - An increasing potential for asset conditions to affect the services it (or they) provides. - Approaching the end of service life. - The condition is below the standard and a large portion of the system (or asset) exhibits significant deterioration. - Significant defects and/or wear. AND/OR ERUSL is 1-5 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Very Poor'. - Unfit for sustained service. - Near or beyond its expected service life and shows widespread signs of advanced deterioration. - The asset or some assets may be unusable. - Severe defects and/or wear AND/OR ERUSL <1 year or beyond EURSL (When estimating condition based on age or according to condition assessment information) | Where municipalities may not already have their own rating system for mechanical and electrical assets this is an optional rating system that can be used or modified. To be used on assets with an estimated service life of at least 20 years. Determine asset conditions using available data, including: - Age and estimated remaining useful service life - Visual inspections - Condition assessments/testing of electrical and mechanical equipment - Maintenance history When using asset age to estimate asset condition, consider maintaining a conservative estimate of the total useful service life until such time as condition assessments data becomes available. The evaluation descriptions (except in italics) are consistent with the "2019 Canadian Infrastructure Report Card". The defect/wear descriptions (in italics) and ERUSLs are for additional information. There is no requirement under O.Reg 588/17 for reporting these assets using this ALOS rating system; however, an ALOS rating and reporting system will be required to meet the future reporting requirements under O.Reg 588/17.
Wastewater treatment, collection and storage civil assets such as: - Process treatment tanks/channels, chambers - Wet and dry Wells (Excluding building envelope (see Building ALOS)), | Targets, ranges and descriptions intended for assets with an estimated useful service life of at least 20 years. A target of "Good" or ERUSL = 11-20 years (when estimating condition based on age) is recommended for the assets/asset systems due to a variety of factors: - a significant to high importance to community services - a significant risk liability (health and safety, environment, financial cost, municipal reputation) - the potential complexities and additional time necessary to plan and design the replacement or rehabilitation of the assets/asset systems (say >5 years) - the potentially significant financial value of the assets/asset systems requiring extra time to accumulate necessary financing for possible full replacement or reconstruction (say >5 years) - some assets can benefit from rehabilitation strategies to extend asset life and defer reconstruction/replacement costs before the assets become too worn or dysfunctional to make such strategies feasible - the assets/assets systems may be expensive to operate and need to be efficient to minimize costs A target of "Fair" or ERUSL = 6-10 years (when estimating condition based on age) may be considered due to a variety of factors: - a moderate or low importance to service delivery - a moderate or low risk liability (health and safety, environment, financial cost, municipal reputation) - there is little complexity or uniqueness to the assets/asset systems thus requiring less planning and design time (< 5 years) - a moderate or low value to replace, reconstruct or rehabilitate the assets/asset systems thus requiring a shorter time to accumulate necessary financing (say < 5 years) - proactive rehabilitation strategies are generally not cost-effective or non-existent and the assets/asset systems are better suited to a straightforward change-out or replacement. - Operating costs are relatively low | The assets are rated 'Very Good'. - Fit for the future. - Well maintained, in good condition, new or recently rehabilitated. - Minor defects and/or wear AND/OR ERUSL>20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Good'. - Adequate for now. - Modest defects and/or wear. AND/OR ERUSL = 11-20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Fair'. - Shows signs of deterioration and some elements exhibit deficiencies. - May require attention. - Moderate defects and/or wear AND/OR ERUSL= 6-10 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Poor'. - An increasing potential for asset conditions to affect the services it (or they) provides. - Approaching the end of service life. - The condition is below the standard and a large portion of the system (or asset) exhibits significant deterioration. - Significant defects and/or wear. AND/OR ERUSL is 1-5 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Very Poor'. - Unfit for sustained service. - Near or beyond its expected service life and shows widespread signs of advanced deterioration. - The asset or some assets may be unusable. - Severe defects and/or wear AND/OR ERUSL <1 year or beyond EURSL (When estimating condition based on age or according to condition assessment information) | Where municipalities may not already have their own rating system for civil/structural assets this is an optional rating system that can be used or modified. To be used on assets with an estimated service life of at least 20 years. Determine asset conditions using available data, including: - Age and estimated remaining useful service life - Visual inspections - Condition assessments/testing of electrical and mechanical equipment - Maintenance history When using asset age to estimate asset condition, consider maintaining a conservative estimate of the total useful service life until such time as condition assessments data becomes available. The evaluation descriptions (except in italics) are consistent with the "2019 Canadian Infrastructure Report Card". The defect/wear descriptions (in italics) and ERUSLs are for additional information. There is no requirement under O.Reg 588/17 for reporting these assets using this ALOS rating system; however, an ALOS rating and reporting system will be required to meet the future reporting requirements under O.Reg 588/17.
*Notes: 1. | Likelihood of Failure is based on the estimated remaining timespan that assets, asset components or asset systems are expected to function at levels that are still adequate, safe, reliable and viable to provide desired Community Levels of Service (CLOS) but at increasing levels of risk as assets/asset components degrade as the end of service life approaches. The total lifespan of an asset often extends beyond estimated useful service life; however, the assets may no longer be sufficient, safe, viable, economical or reliable to provide safe and desired community services. Note that Likelihood of Failure provides high level estimates for strategic risk assessments purposes and can vary on an asset by asset basis according the environment, soil conditions, design, materials and use.
2. | Condition ranges and Likelihood of Failure estimates are intended for strategic analysis and planning and can vary by municipality and by the assets themselves according design, construction, materials, use and environmental conditions.
3. | ERUSL = Estimated remaining useful service life.

## 5, General Performance Ratings
Asset Performance Ratings and Corresponding Likelihood of Failure (All Assets)1, 2
LoF | Very Unlikely Current Likelihood of Failure >10% | Unlikely Current Likelihood of Failure = 10%-30% | Possible Current Likelihood of Failure = 30%-60% | Likely Current Likelihood of Failure = 60%-90% | Very Likely or Certain Current Likelihood of Failure <90%
Perf. | VERY GOOD | GOOD | FAIR | POOR | VERY POOR
General Descrip. | Exceeds or fully meets performance requirements. No affect to services | Meets performance requirements. No affect to services | Just meets performance requirements with some limitations Minor or no perceivable affects to services. | Does not meet several performance requirements in whole or in part. Perceivable and/or sporadic affects to services | Does not meet many or most performance requirements as a whole. Moderate or significant and/or ongoing affects to services.
Operational Functionality | - Fully meets or exceeds current minimum community service level requirements in a fully efficient and effective manner. - Exceeds minimum current design and/or safety requirements - No operational problems experienced. - No affects on community service levels or stakeholders - Fully complies with current Regulations and/or Standards3. - No desirable elements are missing, and all required elements are present. - Technology is state-of-the art/best available - Resource consumption: 100% of baseline efficiency | - Meets current minimum community service level requirements in an efficient and effective manner. - Meets minimum current design and/or safety requirements - Occasional operational problems may be experienced. - No noticeable affects on overall community service levels and/or stakeholders - Complies with Regulations and/or Standards3 with possibly some "grandfathering" where permitted by Regulation for certain standards. - A few desirable elements may be missing, but all required elements are present. - Technology is industry standard - Resource consumption: 91% to 100% of baseline efficiency | - Just meets/essentially satisfies the current minimum community service level requirements with possibly occasional or minor constraints, and/or some inefficiencies and ineffectiveness present. - Just meets minimum current design and/or safety requirements possibly with some added monitoring, extra controls or maintenance. - Operational problems may occur more frequently. - There may be some minor affects to community service levels and/or stakeholders - Meets essential Regulations and/or Standards3 with "grandfathering" where permitted by Regulation for certain standards. - A few desirable elements and one or two required elements are missing. - Technology is adequate but may not be efficient. - Resource consumption: 76 to 90% of baseline efficiency | - A limited ability to meet current minimum community service level requirements with performance frequently below minimum service and efficiency requirements. - Does not fully meet minimum current design and/or safety requirements in whole or in part. Significant monitoring, extra controls or maintenance actions may be required to maintain community services. - Significant operational problems are evident and occur frequently with perceivable and possibly moderate affects to community services - May not meet or partially meets essential Regulations and/or Standards3 which may not be permitted "grandfathering" by Regulation or are unsafe or impractical to continue "grandfathering" - Several desirable elements and one or two required elements are missing. - Technology is nearing obsolescence. May be inefficient, prone to breakdown with no vendor support or original equipment manufacturer parts available. - Resource consumption: 51 to 75% of baseline efficiency | - Ability to meet current minimum community service level requirements is deficient and unsustainable with performance significantly and continuously below minimum service and efficiency requirements. - Does not most or all meet minimum current design and/or safety requirements in whole. Monitoring, extra controls or maintenance actions are not practical or feasible to maintain community services. - Operational problems are serious and ongoing and affecting community services. - Does not meet essential or critical Regulations and/or Standards3, and "grandfathering" cannot be permitted either by Regulation or due to safety or practical concerns. - Many desirable and several required elements are missing. - Technology is obsolete and/or non-functional and replacement parts may be unavailable - Resource consumption: Less than 50% of baseline efficiency
Capacity to Meet Demands | - Capacity fully meets or exceeds current demands and minimum community service level requirements - No operational problems experienced. - No affects on community service levels or stakeholders | - Capacity meets current demands and minimum community service level requirements - Minor and occasional operational problems may be experienced. - No noticeable affects on overall community service levels and/or stakeholders | - Capacity just meets/essentially satisfies current demands and minimum community service level requirements, possibly with occasional or minor constraints and/or reduced efficiency. - Operational problems may occur more frequently. - There may be some minor or modest affects to community service levels and/or stakeholders | - Capacity is frequently below demands and/or minimum community service level requirements. - Significant operational problems are evident and can occur frequently. - There are noticeable and possibly moderate affects to community service levels and/or stakeholders. | - Capacity is significantly and continuously below demands and/or minimum community service level requirements. - Operational problems are serious and ongoing. - There are noticeable and possibly significant affects to community service levels and/or stakeholders.
Operational Resiliency | - Fully meets or exceeds the minimum emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Maximum protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Meets the minimum emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Adequate protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Provides acceptable but limited emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Reasonable but limited protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Provides partial but inadequate emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Partial protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Provides marginal or no emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Marginal or no protection or security from acts of vandalism, trespassing, theft, assault or terrorism.
Environmental Resiliency | - Assets are fully resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Fully meets climate change mitigation requirements. | - Assets are adequately resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Meets almost all climate change mitigation requirements. | - Assets are resilient with some limitations to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Provides acceptable but limited protections from climate change. | - Asset resiliency to environmental stresses is partially lacking; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Provides partial but inadequate protections from climate change. | - Asset resiliency to environmental stresses is mostly or completely lacking; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Provides marginal or no protections from climate change
Notes: 1. | "Likelihood of Failure" is estimated as a percentage based on current status of asset performance.
2. | When assessing Performance of an entire Asset Class, rate where the balance of the assets score (either under one rating or between several).
3. | "Standards" can include measures set through internal poli+A5:F11cy, be an industry guideline, health and safety standard, a design, material or appearance standard, be a factor or measure as part of an Asset Levels of Service, or be an Asset Level of Service itself.

## 6. Wastewater Perf Criteria
Asset Types | Notes on Performance Asset Levels of Service | ALOS | Criteria to Support ALOS Target1,2
- Trunk Sewers - Collection sewers - Forcemains | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement at the earliest practical opportunity. | Operational Functionality | Efficient and effective service delivery: - Minimum pipe diameters of 200mm (Collection Sewers only) - Minimum and maximum pipe flow velocities (i.e. 0.6m/s (2 ft/s) to 3m/s (10ft/s) to reduce pipe wear, pipe displacement, hydrogen sulfite (H2S) generation and provide adequate scour - Sufficient ventilation of gases from the sewer network system to prevent combustible gases and hydrogen sulphide corrosion - Adequate depth to prevent hydraulic surcharging into basements and the environment - Minimization of storm water connections/inflows to improve treatment and collection capacity and efficiencies and reduce treatment plant bypass events.
|  | Capacity to Meet Demands | Capacity to meet minimum service demands: - Sufficient pipe capacities to meet peak design flows and design extraneous (storm and groundwater) inflows
- Pumping Stations/ Pumping Systems - Standby Power | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement at the earliest practical opportunity. | Operational Functionality | Efficient and effective service delivery and compliance with standards: - Efficient design and operations of pumps, dry/wet wells, piping and valves for minimum and maximum flow conditions - Technology is efficient - Compliance with Provincial and Municipal Codes (Ministry of Labour, Building, Fire and Electrical) and Confined Spaces Regulation (Ontario Regulation, or O. Reg. 632/05) made under the Occupational Health and Safety Act (OSHA)
|  | Capacity to Meet Demands | Capacity to meet minimum service demands: - Sufficient pumping station and forcemain capacity to pump and discharge the design peak instantaneous sewage flow (including design extraneous inflows: storm and groundwater)
|  | Operational Resiliency | Process Resiliency: - Capacity to meet maximum instantaneous flows with largest units out of service ("firm" station capacity including forcemains) Back-up capacity/units for critical pumping station processes including: - Standby power generation as required - Emergency storage as required - Fully operational and accessible during a 25-year flood event - Adequate site and facility security
|  | Environmental Resiliency | - Sewage pumping station structures and electrical and mechanical equipment protected from physical damage by a 100-year design flood event - Climate change adaptation measures are in place
- Pre-Treatment/Pre-Treatment Systems - Primary Treatment/ Primary Treatment Systems - Secondary Treatment/Secondary Treatment Systems - Aeration and Disinfection Systems - Biosolids Treatment/Biosolids Treatment Systems - Standby Power - Process treatment tanks, channels, chambers and lagoons | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement at the earliest practical opportunity. | Operational Functionality | Efficient and effective service delivery and compliance with standards: - Treatment design and operations are efficient - Current systems and technology are efficient - Efficient chemical application and disinfection processes - Does not exceed maximum treatment process velocities - Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical).
|  | Capacity to Meet Demands | Capacity to meet minimum service demands: -Treatment process capacity should be such that the treated effluent would continuously meet the established quality criteria in terms of concentrations and loadings (CoA) during the design period - Outflow capacity is 100% of plant receiving capacity
|  | Operational Resiliency | - Critical treatment processes provided with multiple units so that with the largest unit out of operation, the hydraulic capacity of the remaining units should be sufficient to handle the appropriate design sewage flows Maintain treatment capacity during emergency event/failure of treatment system component including: - Standby power generation capacity for critical processes as required - Emergency pumping capability as required - Emergency storage as required - Adequate site and facility security
|  | Environmental Resiliency | - Treatment facilities are protected from 100 year storm events - Climate change adaptation measures are in place
Notes: 1. | Consider the level of conformance to MOE Design Guidelines for Sewage Works for Operational Functionality, Capacity to meet Demands, Operational and Environmental Resiliency in the context of the "General Performance Ratings".
2. | This evaluation can be used: a) To inform a high-level "desktop exercise" to generally measure the ability of the asset classes to meet community service levels, or, b) To measure the performance of asset systems or assets to determine risk to services and the priority and scope of improvements. Independent professional assessments, flow measuring/monitoring and hydraulic modelling may be required, where practical and desirable to investigate asset class or individual asset compliance to ALOS criteria and levels of potential risk.

## 7. WW Asset Class Perf. Eval.
Asset Classes/Types7 | ALOS | Context for Evaluating Performance Criteria1 | Criteria to Support Proposed ALOS Target1, 2 (where information is available) | Weightings based on importance to ALOS4, 5 (Optional) | Distribution of Asset Ratings for each ALOS2, 3
[5 empty] | % Very Good | % Good | % Fair | % Poor | % Very Poor | % NA | TOTAL
Trunk Sewers | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Minimum and maximum pipe flow velocities (i.e. 0.6m/s (2 ft/s) to 3m/s (10ft/s) to reduce pipe wear, pipe displacement, hydrogen sulfite (H2S) generation and provide adequate scour
- Sufficient ventilation of gases from the sewer network system to prevent combustible gases and hydrogen sulphide corrosion
- Adequate depth to prevent hydraulic surcharging into basements and the environment
- Minimization of storm water connections/inflows to improve treatment and collection capacity and efficiencies and reduce treatment plant bypass events.
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Sufficient pipe capacities to meet peak design flows and design extraneous (storm and groundwater) inflows
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
Collection Sewers | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Minimum pipe diameters of 200mm.
- Minimum and maximum pipe flow velocities (i.e. 0.6m/s (2 ft/s) to 3m/s (10ft/s) to reduce pipe wear, pipe displacement, hydrogen sulfite (H2S) generation and provide adequate scour
- Sufficient ventilation of gases from the sewer network system to prevent combustible gases and hydrogen sulphide corrosion
- Adequate depth to prevent hydraulic surcharging into basements and the environment
- Minimization of storm water connections/inflows to improve treatment and collection capacity and efficiencies and reduce treatment plant bypass events.
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Sufficient pipe capacities to meet peak design flows and design extraneous (storm and groundwater) inflows
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
- Pumping Stations/ Pumping Systems - Standby Power | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Efficient design and operations of pumps, dry/wet wells, piping and valves for minimum and maximum flow conditions
- Technology is efficient
- Compliance with Provincial and Municipal Codes (Ministry of Labour, Building, Fire and Electrical) and Confined Spaces Regulation (Ontario Regulation, or O. Reg. 632/05) made under the Occupational Health and Safety Act (OSHA)
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Sufficient pumping station and forcemain capacity to pump and discharge the design peak instantaneous sewage flow (including design extraneous inflows: storm and groundwater)
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Capacity to meet maximum instantaneous flows with largest units out of service ("firm" station capacity including forcemains)
- Back-up capacity/units for critical pumping station processes
- Standby power generation as required
- Emergency storage as required
- Fully operational and accessible during a 25-year flood event
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Sewage pumping station structures and electrical and mechanical equipment protected from physical damage by a 100-year design flood event
|  | To what extent are the assets resilient to the affects of climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Environmental Resiliency |  | 0
- Pre-Treatment/Pre-Treatment Systems - Primary Treatment/ Primary Treatment Systems - Secondary Treatment/Secondary Treatment Systems - Aeration and Disinfection Systems - Biosolids Treatment/Biosolids Treatment Systems - Standby Power - Process treatment tanks, channels, chambers and lagoons | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Treatment design and operations are efficient
- Current systems and technology are efficient
- Efficient chemical application and disinfection processes
- Does not exceed maximum treatment process velocities
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical).
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | -Treatment process capacity should be such that the treated effluent would continuously meet the established quality criteria in terms of concentrations and loadings (CoA) during the design period
- Outflow capacity is 100% of plant receiving capacity
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Critical treatment processes provided with multiple units so that with the largest unit out of operation, the hydraulic capacity of the remaining units should be sufficient to handle the appropriate design sewage flows
- Standby power generation capacity for critical processes as required
- Emergency pumping capability as required
- Emergency storage as required
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Treatment facilities are protected from 100 year storm events
|  | To what extent are the assets resilient to the affects of climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Environmental Resiliency |  | 0
Total Performance | [10 empty] | 0
0
Notes: 1. | Consider the level of conformance to MOE Design Guidelines for Sewage Works for Operational Functionality, Capacity toMeet Demands, Operational Resiliency and Environmental Resiliency in the context of the General Performance Ratings (Tab 5).
2. | This evaluation is intended as a "desktop exercise" to evaluate each asset class based on inherent knowledge of the system and its current ability to meet community service levels. Where information or experienced judgement is not available to assess some criteria or the criteria is not applicable, mark "100" under "NA" (Not Available/Applicable) to remove this criteria from the evaluation. Consider if the missing data or information should be included as part of a data collection plan.
3. | Distribute the different performance as a percentage of the entire Asset Class.
4. | ALOS Performance Weightings
Weightings
| 1 | Unimportant
| 2 | Relatively Unimportant
| 3 | Relatively Important
| 4 | Important
| 5 | Very Important
5. | If weightings are to be applied, they must be applied to ALL the asset performance ratings.
6. | If additional rows or columns are required to be added, the sheet needs to be "Unprotected". This will allow formulas to be copied and pasted. There is no password to Unprotect the sheet.
7. | This worksheet should be applied once for each Asset Class and replicated as often as necessary to evaluate each of the Asset Classes.

## 8. WW Asset Perf. Eval.
|  |  |  | Asset Name |  |  | Asset Name |  |  | Asset Name |  |  | Asset Name
Asset Types6 | ALOS | Context for Evaluating Performance Criteria1 | Criteria to Support Proposed ALOS Target1 (where information is available) | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL
Trunk Sewers | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Minimum and maximum pipe flow velocities (i.e. 0.6m/s (2 ft/s) to 3m/s (10ft/s) to reduce pipe wear, pipe displacement, hydrogen sulfite (H2S) generation and provide adequate scour
- Sufficient ventilation of gases from the sewer network system to prevent combustible gases and hydrogen sulphide corrosion
- Adequate depth to prevent hydraulic surcharging into basements and the environment
- Minimization of storm water connections/inflows to improve treatment and collection capacity and efficiencies and reduce treatment plant bypass events.
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Sufficient pipe capacities to meet peak design flows and design extraneous (storm and groundwater) inflows
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
Collection Sewers | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Minimum pipe diameters of 200mm.
- Minimum and maximum pipe flow velocities (i.e. 0.6m/s (2 ft/s) to 3m/s (10ft/s) to reduce pipe wear, pipe displacement, hydrogen sulfite (H2S) generation and provide adequate scour
- Sufficient ventilation of gases from the sewer network system to prevent combustible gases and hydrogen sulphide corrosion
- Adequate depth to prevent hydraulic surcharging into basements and the environment
- Minimization of storm water connections/inflows to improve treatment and collection capacity and efficiencies and reduce treatment plant bypass events.
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Sufficient pipe capacities to meet peak design flows and design extraneous (storm and groundwater) inflows
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
- Pumping Stations/ Pumping Systems - Standby Power | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Efficient design and operations of pumps, dry/wet wells, piping and valves for minimum and maximum flow conditions
- Technology is efficient
- Compliance with Provincial and Municipal Codes (Ministry of Labour, Building, Fire and Electrical) and Confined Spaces Regulation (Ontario Regulation, or O. Reg. 632/05) made under the Occupational Health and Safety Act (OSHA)
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Sufficient pumping station and forcemain capacity to pump and discharge the design peak instantaneous sewage flow (including design extraneous inflows: storm and groundwater)
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | - To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Capacity to meet maximum instantaneous flows with largest units out of service ("firm" station capacity including forcemains)
- Back-up capacity/units for critical pumping station processes
- Standby power generation as required
- Emergency storage as required
- Fully operational and accessible during a 25-year flood event
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Sewage pumping station structures and electrical and mechanical equipment protected from physical damage by a 100-year design flood event
|  | To what extent are the assets resilient to the affects of climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
- Pre-Treatment/Pre-Treatment Systems - Primary Treatment/ Primary Treatment Systems - Secondary Treatment/Secondary Treatment Systems - Aeration and Disinfection Systems - Biosolids Treatment/Biosolids Treatment Systems - Standby Power - Process treatment tanks, channels, chambers and lagoons | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Treatment design and operations are efficient
- Current systems and technology are efficient
- Efficient chemical application and disinfection processes
- Does not exceed maximum treatment process velocities
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical).
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | -Treatment process capacity should be such that the treated effluent would continuously meet the established quality criteria in terms of concentrations and loadings (CoA) during the design period
- Outflow capacity is 100% of plant receiving capacity
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Critical treatment processes provided with multiple units so that with the largest unit out of operation, the hydraulic capacity of the remaining units should be sufficient to handle the appropriate design sewage flows
- Standby power generation capacity for critical processes as required
- Emergency pumping capability as required
- Emergency storage as required
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Treatment facilities are protected from 100 year storm events
|  | To what extent are the assets resilient to the affects of climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
Total Performance
Notes: 1. | Consider the level of conformance to MOE Design Guidelines for Sewage Works for Operational Functionality, Capacity to Meet Demands, Operational Resiliency and Environmental Resiliency in the context of the General Performance Ratings (Tab 5).
2. | ALOS Performance Weightings
Weightings
| 1 | Unimportant
| 2 | Relatively Unimportant
| 3 | Relatively Important
| 4 | Important
| 5 | Very Important
3. | If weightings are to be applied, they must be applied to ALL the asset performance ratings.
4. | ALOS Performance Ratings
| 1 | Very Good
| 2 | Good
| 3 | Fair
| 4 | Poor
| 5 | Very Poor
| 0 | N/A
5. | If additional rows or columns are required to be added, the sheet needs to be "Unprotected". When adding Rows, copy the row and paste between two criteria's by clicking "Insert Copied Row". This will allow formulas to be copied and pasted. There is no password to Unprotect the sheet.
6. | This worksheet can be used to evaluate up to four assets within the same Asset Class and the sheet can be replicated to evaluate additional assets.

## 9. General Asset Evaluation
Asset Name6 | ALOS | Performance Critera1 | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL
| Operational Functionality | Efficiency and effectiveness of service delivery/provision
Ability to meet minimum current design and/or safety requirements
Level of operational problems experienced.
Level of noticeable affects to customers or services due to operational problems
Compliance with current Regulations and/or Standards (including levels of permitted "grandfathering")
Level/number of required elements present.
Relevance and effectiveness of technology
Efficiency of resource consumption
|  | Average Operational Functionality ALOS Rating | 0
| Capacity to Meet Demands | The degree to which capacity satisfies current demands and minimum community service levels
Level of operational problems related to capacity
Level of noticeable affects to customers due to capacity shortfall
|  | Average Capacity to Meet Demands ALOS Rating | 0
| Operational Resiliency | Level of surplus capacity for emergency or extraordinary operating conditions
Level of back-up capacity/units to maintain critical systems and services during emergency conditions.
Availability of alternative sources for emergency service provision
To what extent the assets are secure from acts of vandalism, trespassing, theft, assault or terrorism.
|  | Average Operational Resiliency ALSO Rating | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc..
To what extent are the assets resilient to the affects of climate change.
|  | Average Environmental Resiliency ALOS Rating | 0
Total Performance |  |  |  | 0
Notes: 1. | Consider the level of conformance to Operational Functionality, Capacity to Meet Demands, Operational Resiliency and Environmental Resiliency in the context of the General Performance Ratings (Tab 5).
2. | ALOS Performance Weightings
Weightings
| 1 | Unimportant
| 2 | Relatively Unimportant
| 3 | Relatively Important
| 4 | Important
| 5 | Very Important
3. | If weightings are to be applied, they must be applied to ALL the asset performance ratings.
4. | ALOS Performance Ratings
| 1 | Very Good
| 2 | Good
| 3 | Fair
| 4 | Poor
| 5 | Very Poor
| 0 | N/A
5. | If additional rows or columns are required to be added, the sheet needs to be "Unprotected". When adding Rows, copy the row and paste between two criteria's by clicking "Insert Copied Row". This will allow formulas to be copied and pasted. There is no password to Unprotect the sheet.
6. | This worksheet should be applied once for each asset type and replicated as often as necessary or additional columns can be added for each additional asset in the Asset Class (formulas will be required to be copied over).

## A. WW Summary ALOS Info
ALOS Type | Asset Categories | Rating Method | Distribution by Asset Ratings (Assets as a % of the Total Asset Class) and Corresponding Likelihood of Failure1
|  |  | Very Unlikely <10% | Unlikely 10%-30% | Possible 30%-60% | Likely 60%-90% | Very Likely >90%
Condition | All | Remaining Useful Service Life2 | >20 Years | 11-20 Years | 6-10 Years | 1-5 Years | <1 Year
| Civil Structures, Mechanical & Electrical Equipment | Generic Rating | Very Good | Good | Fair | Poor | Very Poor
|  | Description | - Fit for the future. - Well maintained, in good condition, new or recently rehabilitated. - Minor defects and/or wear | - Adequate for now. - Modest defects and/or wear. | - Shows signs of deterioration and some elements exhibit deficiencies. - May require attention. - Moderate defects and/or wear | - An increasing potential for asset conditions to affect the services it (or they) provides. - Approaching the end of service life. - The condition is below the standard and a large portion of the system (or asset) exhibits significant deterioration. - Significant defects and/or wear. | - Unfit for sustained service. - Near or beyond its expected service life and shows widespread signs of advanced deterioration. - The asset or some assets may be unusable. - Severe defects and/or wear
| Sewer Pipes | PACP | PACP = 1 or 2 | PACP = 3 | PACP = 4 | PACP = 5 | PACP = 5
|  | Description | Very Good or Good Pipe segment has minor defects - pipe unlikely to fail for at least 20 years. | Fair Pipe segment has moderate defects - deterioration may continue, at a ten to twenty year timeframe. | Poor Pipe segment has severe defects - risk of failure within the next five to ten years | Very Poor Pipe segment has failed or will likely fail within the next five years - requires immediate attention. | Failed Pipe segment has failed or will likely fail within the next five years - requires immediate attention.
Performance | All | Generic Rating | Very Good | Good | Fair | Poor | Very Poor
|  | General Description | Exceeds or fully meets performance requirements. No affect to services | Meets performance requirements. No affect to services | Just meets performance requirements with some limitations Minor or no perceivable affects to services. | Does not meet several performance requirements in whole or in part. Perceivable and/or sporadic affects to services | Does not meet many or most performance requirements as a whole. Moderate or significant and/or ongoing affects to services.
Notes: 1. | Likelihood of Failure is an estimate of the timespan (Condition) or the level of viability (Performance) that assets, asset components or asset systems are expected to provide adequate, safe and reliable Community Levels of Service (CLOS) but at increasing levels of risk as assets/asset components degrade as the end of service life approaches.
2. | The total lifespan of an asset often extends beyond Estimated Useful Service Life; however, the assets may no longer be sufficient, safe, viable, economical or reliable to provide safe and desired community services. Note that Likelihood of Failure provides high level estimates for strategic risk assessments purposes and can vary on an asset by asset basis according the environment, soil conditions, design, materials and use.

## B. ALOS Framework
AMONTario Asset Level of Service Framework
Condition Levels of Service (Tab 4) |  |  |  | Performance Levels of Service (Tabs 5-9)
ALOS Measures | Corresponding Likelihood of Failure Measures |  |  | ALOS Measures |  | Corresponding Likelihood of Failure Measures
PCI, BCI, FCI, PACP, General Ratings (“Very Good” to “Very Poor”), Maximum Age, etc. | Risk Ratings | Estimated Timeframe | % LoF | 1. Operational Functionality 2. Capacity to Meet Demands 3. Operational Resiliency 4. Environmental Resiliency | ALOS Rating | Risk Ratings | % LoF
| Very Unlikely | >20 yrs. | <10% |  | Very Good | Very Unlikely | <10%
| Unlikely | 11-20 yrs. | 10%-30% |  | Good | Unlikely | 10%-30%
| Possible | 6-10 yrs. | 30%-60% |  | Fair | Possible | 30%-60%
| Likely | 1-5 yrs. | 60%-90% |  | Poor | Likely | 60%-90%
| Very Likely or Certain | <1 yr. | >90% |  | Very Poor | Very Likely or Certain | >90%

## C. ALOS to CLOS Mapping
ALOS Categories | General ALOS Measurement Criteria | Predominant Community Service Outcomes
|  | Health & Safety | Reliability | Quality | Quantity | Efficiency | Accessibility
Condition | Physical state of the asset measured by condition rating systems (PCI, BCI, FCI, PACP, Number of Breaks, Very Good to Very Poor etc.) | X | X | X | X | X
Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | X | X | X |  | X | X
Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | X | X | X | X | X | X
Operational Resiliency | - To what degree minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. - To what extent the assets are secure from acts of vandalism, trespassing, theft, assault or terrorism. | X | X
Environmental Resiliency | - To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - To what extent are the assets resilient to the affects of climate change. | X | X |  |  |  | X